## Slide 1
February 28, 2025
1.
March 10th, 2026
Presented by
Dustin Deitch
What are Significant Deficiencies, How can they be avoided, and how to resolve them.
Sanitary Survey
Significant
Deficiencies

## Slide 2
What are Significant Deficiencies?

## Slide 3: “SignificantDeficienciesare bad”

## Slide 4: Significant Deficiencies
Examples
Unsanitary Source Conditions
Cross Connections
Unsanitary Storage / Distribution
Inadequate pressure
etc..
NAC 445A.4665
A defect in design, operation, or maintenance. A failure or malfunction of the water system, that the inspector determines poses an actual or potential threat to public health or to the integrity of the drinking water system

## Slide 5: Examples
  Lack of Atmospheric Vacuum Breakers (AVB)s on hose bibs.
  Missing or damaged Sanitary well seal.
  Evidence of flooding around groundwater well.
  Chemical storage near a wellhead with no secondary containment.
  System pressure falling below 20 psi under normal operations.
  No certified operator of appropriate grade.
Some Examples of Significant Deficiencies
6.

## Slide 6: How to Avoid Significant Deficiencies

## Slide 7
Maintain Physical Infrastructure
Keep well pads sealed and repair leaks promptly.
Inspect Storage tank hatches / Paint / Rust spots
Protect Treatment equipment from weather and contamination
Maintain Documentation
Tank Inspection and cleaning records
Cross connection control plans (CCCP)
Operation and Maintenance Manuals (O&M manuals)
Emergency Response Plan
Implement Cross Connection Control
Install proper backflow assemblies where required.
Maintain testing records of backflow devices.
Prohibit unprotected auxiliary water source connections.

## Slide 8
Is there a pathway for contamination?
Is treatment reliably controlled?
Is the operator aware and engaged?
Is there documentation?
Is there follow through?
What Inspectors are really looking for

## Slide 9
Deficiencies
Part of the description will tell what needs to be done to resolve the deficiency.
(Seen in Figure to the right)
How to Resolve
Each Sanitary Survey Letter will outline deficiencies the system received during the survey.
Follow the instructions within the description to resolve the deficiency.
Call your Facility Manager if there are any questions about how to get deficiency resolved.

## Slide 10
Within 30 Days
Consult with BSDW to discuss how to proceed
Timeframe to Resolve
Within 30 Days after fixing
Let us know that you have resolved the issues. Include photographs or other documentation
Within 120 Days
Correct the problem or have a NDEP approved corrective action plan (CAP).
Must meet 3 deadlines below. Failure to do so may result in a treatment technique violation.

## Slide 11
A written plan submitted by a Public Water System (PWS) that describes how and when the system will correct a Significant Deficiency or other compliance issue identified during a sanitary survey or enforcement action.
Corrective Action Plans
(CAPs)

## Slide 12
Description of Deficiency
Clear reference to the Sanitary Survey finding.
Proposed Corrective Action
Specific steps the system will take.
Timeline / Schedule
Expected date to resolve the deficiency.
Responsible Party
Operator, contractor, engineer, board, etc..
What a CAP
Must Include
Supporting Documentation
Engineering Documents / Equipment Specs - (If Applicable).

## Slide 13: Timeframe Expectations of CAPs
Submit a CAP withing 45 days of receiving the Significant Deficiency notification.
Correction is generally expected within 120 days, unless BSDW approves an alternate schedule.
Failure to follow the approved schedule will escalate system to a treatment technique violation / enforcement.

## Slide 14: Thank You
Dustin Deitch
Nevada Division of Environmental Protection
Phone: 775-684-9517
Email: Ddeitch@Ndep.Nv.gov